## Slide 1: What is real, what is simulated, and what the numbers mean
REAL TODAY
The whole path: a signed message goes out, a Victron plant and a Viessmann heat pump react, verified replies come back
The planning and the rule check, running on the fleet every two hours
Measured on streets with cars, heat pumps shedding floor heating too: 16 to 36 % off the evening peak, in line with published smart-charging and home-battery trials (3 to 6 kW per car, 1 to 2 kW per battery at the peak)
SIMULATED
The fleet: 271 simulated households, each standing for 8 real ones: 2,184 houses with a 10 to 25 kWh battery, 1,190 of them with an 11 kW charger needing 6 to 26 kWh a night
The "without" curve is the same houses left alone: a car charges on 55 % of nights, people come home over three hours, full power until full. Nothing inflated
These houses carry about 30 % of a street's evening load: a 2030 picture, not a street today
−176 kW
one street, Speising-22: 574 → 398 kW at the evening peak, 31 %, measured tonight
−5.2 MW
Vienna with 2,184 enrolled houses: 26.6 → 21.7 MW at the evening peak, 19 %, measured tonight
0 kW
on a street where no car charged tonight: the gap is the cars and the batteries, nothing else
1
real house in the fleet tonight. The fleet is the part we are asking you to build
Notes: 3:30-3:55. Real: the whole path, a Victron plant and a Viessmann heat pump reacting to a signed message, the planning on the fleet. Simulated: the fleet, two thousand houses, same cars with and without, realistic charging. Measured tonight: one street thirty-one percent off its peak, Vienna with two thousand houses five megawatts off, a street where no car charged, zero.

## Slide 2: Six signals, one grammar: limits for a window
PREPARE
Fill the battery, the car and the tank to a target by a deadline, in the quiet hours
ABSORB
PV surplus: cap export, charge, soak it into the car and the hot water, curtail last
SUPPORT
Peak or deficit: "take 3 kW only", and if the street needs more, "give at least 2 kW"
STRETCH · vision
Street is dark: grid-forming inverters island the street, batteries are rationed until restoration, export locked to zero. Today's home inverters cannot form a grid; the signal is ready for the ones that will
RECOVER
After restoration: staggered recharge so the street does not refill at once
RELEASE
Event over. Owner mode, immediately
Envelopes: a SUPPORT or ABSORB carries one ceiling per 15-minute slot, the meter's settlement interval. Cohorts let one signal address half a street, so the other half exports while the first charges.
Notes: Appendix, for questions. Do not read all six. Point at SUPPORT and ABSORB, the everyday ones, PREPARE and RECOVER, the crisis ones, and name STRETCH as the vision: a street that keeps its lights on from its own basements needs grid-forming inverters, which are arriving. The protocol already has the signal for them.

## Slide 3: The household is the unit: everything behind one meter, one agent, eight functions
Battery
the lever of last resort: discharge to cover the house or feed the street, within the owner floor
EV charger
the first lever: throttled 16 to 6 A under a cap, soaks surplus, paused when the street is dark
Heat pump
second lever: tank to 55 °C and room +2 K under surplus, tank 40 °C and room −2 K under a cap, 3 kW shed per house
Boiler
same rules at 65 and 45 °C; an electric boiler is a kilowatt-hour sponge
The agent, any language, forty lines
Pin the platform key at registration
Subscribe to the segment topics, outbound only
Verify signature, sequence, freshness, scope
Merge with owner limits: floor, caps, opt-out
Apply: the only vendor-specific step
Ack, signed with the device key
Watch the heartbeat and the window
Revert to owner mode
Blatnica, the real one: Victron Cerbo GX with MultiPlus-II and a 15 kWh battery, an 11 kW Victron EV station, and a Viessmann Vitocal heat pump via ViCare. One house on the board.
Notes: Appendix, for questions. The vendor only owns step five. Everything else is identical on the Victron, on the ViCare cloud agent and on the 270 simulated houses.

## Slide 4: DeepSeek runs the grid every 15 minutes. The guard is the brake
SENSE
72 transformers, 90-minute forecast, trigger at ±85 % of rating
DEEPSEEK DECIDES
DeepSeek-V4.1-Flash on the DGX Spark proposes mode, segment, cap, window and a dynamic envelope, in ~3 s
GUARD
deterministic policy: window, depth, rate, reverse rating, cooldowns. Not AI. Refuses or passes
SIGN + PUBLISH
Ed25519, one topic per segment, over TLS. Houses merge with owner limits and ack
Three modes: autonomous, operator approves, off. In autonomous mode nothing waits for a human; the guard and the device-side bounds are the safety
Scope is physics: a street transformer is relieved only by its own houses; a feeder or substation by every house under it; a village can feed its neighbours through the 22 kV line
Every decision is logged with its reasoning, latency, verdict and the acks it earned. That log is the audit trail
Notes: Appendix, for questions. AI proposes, guard disposes. Say it twice. Then: why the guard is not AI.

## Slide 5: Everything on that screen runs on real infrastructure today
272
households on the board, 8,070 houses represented
72
street transformers, 24 feeders, 8 substations with Wiener Netze names
2
real devices: a Victron plant and a Viessmann heat pump, 60 km from here
~3 s
DeepSeek decision latency on the DGX Spark
Real plant
Cerbo GX on Venus OS Large, a 53-node Node-RED agent we deploy over the admin API; EV Charging Station throttled first; ESS limits written and restored
Heat pump
Vitocal CU401B through the ViCare REST API with a refresh token; hot-water setpoint and one-time charge, verified on the unit
Transport
Mosquitto on our own server, Let's Encrypt, TLS only, credentials and topic access lists; devices open outbound connections only
Platform
FastAPI on a Ubuntu box behind Apache and Let's Encrypt; registry tree, guard, signing, history, autopilot; public board at gridzilla.victronlab.sk
Simulation
262 households with battery, PV, EV commutes, heat pumps and boilers with real tank physics; each agent speaks the same protocol as the Cerbo
Protocol
Frozen as PROTOCOL.md with JSON Schemas for envelope, signal and ack; any vendor can implement the eight functions from it
Notes: Appendix, for questions. The point of this slide is credibility: nothing is a mock-up. Name the two real devices and the public broker.

## Slide 6: Any vendor, four lines each. Any household, paid on the meter
Three paths to the same agent
Vendor cloud: GoodWe SEMS, Huawei FusionSolar, SolarEdge, Tesla Fleet, SMA, Fronius. Export limit, discharge to cover load, forced discharge schedule, grid charge schedule
Local controller: Home Assistant, EVCC, OpenEMS, SunSpec Modbus. What the demo runs on Node-RED today
Standards gateway: EEBus LPC and LPP are literally our import and export caps; OpenADR 3, IEC 61850, OCPP 2.0.1 for chargers
GoodWe is one apply function away: the registers and the hardware are on the team
Why a DSO pays and a household joins
Limits are verifiable, reductions are not: the DSO's own smart meter answers yes or no per 15-minute interval. No baseline to inflate
No ack, no pay; compliance gates the perks; the DSO's existing disconnect is the backstop in a crisis
The hook: a dynamic export limit beats today's static cap on all but a few afternoons, and gets a refused connection approved
Plus an availability fee, per-kWh payment for forced feed-in, a full battery before an outage, and a shorter shedding queue
Noon export is worthless when everyone exports; the same kilowatt-hours leave at six, paid
Notes: Appendix, for questions. Left: vendor independence is proven by the simulators, which run no Victron code. Right: the economics in two sentences, pay on the meter and the dynamic connection.

## Slide 7: Production at a DSO: the effort, the cost, the saving
EFFORT
Protocol and agents are the small part; they exist
The DSO must add: enrolment bound to the meter point and operator login, a PKI with key rotation, settlement on meter data, the real network model feeding the tree and ratings, 24/7 operations, NIS2 and energy-law compliance
10-house pilot on one transformer: 3 months
A district of a few thousand homes: 12-18 months, 6-8 people, roughly 1.5-3 M€ including the security audit
COST TO RUN
The platform is cheap: two servers and a broker
The real cost is the incentive: a flat 100-200 € per enrolled house per year, plus energy at crisis prices during STRETCH and SUPPORT
Paid only to houses whose meter proves they followed the signal. No enforcement, no payment, no saving
SAVING
Street transformer upgrade 50-150 k€, feeder reinforcement hundreds of k€, a substation tens of M€
Every street held at ~70 % at the evening peak defers the reinforcement the EV and heat-pump wave otherwise forces this decade
Vienna scale: hundreds of M€ of capex deferred against a few M€ a year of incentives
Plus a tool for the outage: PREPARE before it, RECOVER after it, and with grid-forming inverters STRETCH keeps a dark street alive from its own batteries
Notes: Appendix, for questions. Our numbers, not a quote. The point is the shape: small platform, incentive is the real opex, capex deferral is the saving, and enforcement on the meter is what makes the saving real.

## Slide 8: What the flattening looks like: speising-22, 400 kVA, from an earlier run
−199 kW
largest cut below the counterfactual on this transformer
2 kW
import cap per house DeepSeek chose; EVs throttled first, batteries second
0
owner floors crossed; partial acks where a battery hit its reserve
Notes: Appendix, for questions. Grey is what the same houses would have drawn, blue is what they drew, red is the transformer. The gap is the product. Real numbers from the running system, 8 houses per simulated household.

## Slide 9: Security of the control plane: the DSO can ask, it can never command
Authenticity
every signal, heartbeat and ack carries an Ed25519 signature; the device pins the platform key and signs with its own
Replay
monotonic sequence numbers persisted on the device, 120 s freshness, heartbeats with sequence and timestamp
Bounded
limits, never setpoints; four-hour window enforced on the device itself; depth and rate capped by the guard
Owner veto
minimum SoC, max current, opt-out merged on the device; a compromised DSO key moves nothing past them
Fail-safe
window end, heartbeat loss or RELEASE restore the owner's settings; a dead platform leaves every house in owner mode
Transport
TLS with a real certificate, per-role credentials, topic ACLs; a device cannot publish a signal even if it tried
Named before you ask
Enrolment is open, any device id can register a key; production binds it to the meter point with a one-time code. The operator board has no login for the demo; production is SSO plus a two-person rule for feeder-level signals. Neither changes the protocol.
Notes: Appendix, for questions: the security slide. Six controls, then the two gaps yourself. A juror who finds a gap you named is on your side.